Applicant ___________________________  App#___________

Lot____ No._____ Street ______________________________

Suburb _______________________________

EHO ____________________________ Date _____________

Final Inspection of ATU’s

|  | Aerobic Treatment Unit (ATU) | / |
| --- | --- | --- |
| 1 | Confirm septic tanks have been full for 24 hours |  |
| 2 | Check water levels in all chambers of the ATU |  |
| 3 | Visually check to see if growth media is in position |  |
| 4 | Switch on blowers / aerator and check aeration of chamber |  |
| 5 | Check sludge return is operational |  |
| 6 | Check skimmer return is operational |  |
| 7 | Check chlorine dispenser(s) is full and in position |  |
| 8 | Check high water level float and blower / aerator alarm(s) in house, or visible from house. |  |
| 9 | Ensure that all fittings and protective covers are secured |  |
|  | Irrigation Area |  |
| 10 | Check that the irrigation area is sized correctly |  |
| 11 | Pad height to be at least 500mm above highest known water table |  |
| 12 | Check set back requirements from open & closed fenced boundaries |  |
| 13 | Check set back requirements from buildings |  |
| 14 | Check set back requirements from sub-soil / open drains |  |
| 15 | Check set back requirements from swimming pools |  |
| 16 | Check set back requirements from bores / wells / creeks |  |
| 17 | Check set back requirements from ATU’s |  |
| 18 | Check set back requirements from paths, driveways, carports and other structures |  |
| 19 | Check irrigation spray - height 600mm max - area 3m radius - sprayers face inwards onto disposal area |  |
| 20 | Check dripper irrigation – separate feed and flushing manifolds - flushing manifold fitted with flush valve at lowest point - vacuum breaker valve fitted at highest point in the system - dripper lines fixed in position & 600mm(sand)/1m(clay) apart. |  |
| 21 | Disposal area to be retained if required |  |
| 22 | Mulch material to be distributed over the area and plants to be planted into position |  |
| 23 | Warning signs to be placed in position |  |
|  | General |  |
| 24 | Confirm that installation corresponds to approved plan |  |
| 25 | Is as constructed plan required? |  |
| 26 | Mosquito proof cowl fitted to vent pipe |  |
| 27 | Certificate of compliant installation received |  |
| # | Comments |  |

# The Effluent Disposal Area Shall Comply With The Following Minimum Setbacks:

| ## Item | ## Spray irrigation | ## Sub-strata irrigation | ## Sub-surface irrigation | ## Aquarius Aquasafe Drains |
| --- | --- | --- | --- | --- |
| ## Open Fenced Boundaries | ## 1.8 metres | ## 0.5 metres | ## 0.5 metres | ## 1.8 metres |
| ## Closed Fenced Boundaries ## a minimum of 1.2m high | ## As determined by the local government | ## 0.5 metres | ## 0.5 metres | ## 1.8 metres |
| ## Buildings | 1.8 metres ** | ## 0.5 metres | ## 0.5 metres | 1.8 metres |
| ## Sub-soil/ Open drains | ## 6.0 metres | ## 3.0 metres | ## 3.0 metres | ## 6.0 metres |
| ## Swimming Pools | ## 3.0 metres *** | ## 2.0 metres | ## 2.0 metres | 1.8 metres |
| ## Bores/Wells/Creeks | ## 30.0 metres | ## 30.0 metres | ## 30.0 metres | ## 30.0 metres |
| ## ATUs | ## 1.8 metres | ## 0.5 metres | ## 0.5 metres | ## 1.8 metres |
| ## Paths, driveways, carports and other structures | ## 1.8 metres | ## 0.5 metres | ## 0.5 metres | ## 1.8 metres |

**	Where the site has a severe slope and a building (including those on adjoining lots) is downhill from the effluent disposal area, this setback is altered to 3.0 metres.

***Where the site has a severe slope and a swimming pool (including those on adjoining lots) is downhill from the effluent disposal area, this setback is altered to 6.0 metres.

# The minimum depth from the upper surface of a surface irrigation area to the highest known water table is 500mm.

# The minimum depth from the invert of the discharge pipe of a sub surface or sub soil irrigation area to the highest known water table is 500mm.

We would suggest that it would be appropriate where the applicant is not the premise owner, that the property owner also be provided a copy of the “Approval to Construct or Install”, plus these Conditions of Approval and all attached documentation.