Applicant ___________________________  App#___________

Lot____ No._____ Street ______________________________

Suburb _______________________________

EHO ____________________________ Date _____________

Final Inspection of Septic Tanks and Leach Drains

| # | Septic Tanks | / |
| --- | --- | --- |
| 1 | Confirm septic tanks have been full for 24 hours |  |
| 2 | Septic tanks are not leaking (< 10% fall in level in 24 hours) |  |
| 3 | Base of septic tanks are solid |  |
| 4 | Depth of septic tanks (1065mm) |  |
| 5 | Drop across 1520mm septic tank (100mm) |  |
| 6 | Check squares are in, opposite each other and correct length (500mm) |  |
| 7 | Inlets & outlets cemented both sides |  |
| 8 | Septic tanks 1.2m from buildings, boundaries etc |  |
| 9 | Depth to lids (300mm) |  |
| 10 | If pump install is alarm (audio/visual) installed and working |  |
|  | Leach Drains |  |
| 11 | Check length of leach drains (2 x___m) |  |
| 12 | Leach drains 1.8m from buildings, boundaries, driveways etc |  |
| 13 | 1.8m between leach drains, unless otherwise approved |  |
| 14 | Leach drains 6m from open/subsoil drains & soak wells |  |
| 15 | Leach drains not subject to stormwater inundation (eg from downpipes, or runoff) |  |
| 16 | Leach drains 30m from water course, bore, dam, wetland etc |  |
| 17 | Leach drains are installed with lids at NGL to 300mm below or as approved |  |
| 18 | Effective depth & width of leach drains (0.6m x 0.6m) |  |
| 19 | Where in laterite, check rock fractured to depth of 600mm below base |  |
| 20 | Check geotextile cloth for non-standard drains |  |
| 21 | Check blue metal/aggregate (300mm) and sand fill (1.5m), by probe |  |
| 22 | Check bund for inverted leach drains (1m wide, keyed in 300mm) |  |
| 23 | Check diverter |  |
| 24 | Check gaps between segments, large gaps (>1cm) to be cemented |  |
|  | General |  |
| 25 | Confirm that installation corresponds to approved plan |  |
| 26 | Is as constructed plan required? |  |
| 27 | Mosquito proof cowl fitted to vent pipe |  |
| # | Comments |  |