Sizing Non-Standard Septic Tanks and Leach Drains and ATU’s

8 & 29)

Septic Tanks (Reg.28&29)

Residential

5 Bedrooms or less

A standard set of precast concrete septic tanks, consisting of a 1520mm and a 1220mm diameter tank (total vol. approx 3180L) will be sufficient for up to 5 bedrooms.

More than 5 Bedrooms*

…..… No. bedrooms

x 	270L

= ________

+    1820L

=________ L Required vol.

Sheds & Garages – For sheds or similar with a shower and toilet where the premises already has a full system, a 1520mm septic tank and 1x6m drain may be acceptable, dependant on site conditions.

*See Approved Plastic Tank Suppliers Info Sheet for details of non standard sized plastic tanks.

Non Residential

Blackwater System  (toilets only)

_______   type of premises

……….	     L/day (from R29 table)

x 	 ……….      No. of people

= ________ Tot. L/day

+    1360L (do not need to add for ATU)

=________ L Required vol.

Combined System  (all waste)

_______   type of premises

……….	     L/day (from R29 table)

x 	 ……….      No. of people

= ________ Tot. L/day

+    1820L (do not need to add for ATU)

=________ L Required vol.

Leach Drains (Reg. 49&50)

Residential

See Table in Reg 49 and the table on the following page

Non Residential

Alternating (use this for non-residential even if it is not an alternating system)

………. vol wastewater/day

÷  20  (or 30 if sandy soil)

= ______

÷ …….. IA – see table below

=  _____m( total length)

÷   2

=  2 x ______m drains

÷ ……..  segment length (see table)

= _____ number of segments/drain

Non-Alternating (only use for residential non-alternating system)

………. vol wastewater/day

÷  10  (or 15 if sandy soil)

= ______

÷ …….. IA – see table below

=  _____m( total length)

ATUs servicing leach drains

………. vol wastewater/day

÷ 50 (or 100 if sandy soil)

=__________

÷…….IA – see table below

= ____m total length.

ATUs servicing irrigation

………. vol wastewater/day

÷ 10 =

________sqm of irrigation area required

| Drain Type | IA (Infiltrative Area) m2 | Segment Length (m) |
| --- | --- | --- |
| Std Concrete | 1.6 | 1.2 |
| Plastic Drains* |  |  |
| Atlantis** | 1.34 | 0.61 |
| Atlantis Matrix*** | 1.3 | 0.685 |
| ADM**** | 1.19 | 0.356 |
| Everglas#230 | 0.89 | 1.5 |
| Everglas#350 | 1.15 | 1.5 |
| Everglas#410 | 1.28 | 1.5 |
| Filtrex LD Cage | 0.9 | 1.2 |
| Reln - jumbo | 1.31 | 1.517 |
| Reln - lge | 1.23 | 1.517 |
| Reln - std | 0.92 | 1.517 |
| *Effluent to enter through top of drain |  |  |
| **Extra 0.38m2 provided by end plates |  |  |
| ***Extra 0.37m2 provided by end plates |  |  |
| ****Extra 0.30m2 provided by end plates |  |  |

| No. bedrooms | Plastic Leach Drain Lengths |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Std | Atlantis | Atlantis Matrix | ADM | Everglas#230 | Everglas#350 | Everglas #410 | Reln - Jumbo | Reln - Lge | Reln - Std |
|  | Sandy Soils |  |  |  |  |  |  |  |  |  |
| 2 or less | 2 x 6m | 2 x 6.7m | 2 x 6.9m | 2 x 7.6m | 2 x 11m | 2 x 9m | 2 x 8m | 2 x 7m | 2 x 8m | 2 x 10m |
| 3 | 2 x 8m | 2 x 9.1m | 2 x 9.5m | 2 x 10.4m | 2 x 15m | 2 x 12m | 2 x 10m | 2 x 9.5m | 2 x 10m | 2 x 14m |
| 4 or more | 2 x 9m | 2 x 10m | 2 x 10.3 | 2 x 11.3m | 2 x 17m | 2 x 13m | 2 x 11m | 2 x 10.5m | 2 x 11m | 2 x 15m |
|  | Gravel & Loam Soils |  |  |  |  |  |  |  |  |  |
| 2 or less | 2 x 9m | 2 x 9.9m | 2 x 10.6m | 2 x 11.6m | 2 x 17m | 2 x 13m | 2 x 11m | 2 x 11m | 2 x 11m | 2 x 15m |
| 3 | 2 x 12m | 2 x 13.3m | 2 x 14.4m | 2 x 15.8m | 2 x 22m | 2 x 17m | 2 x 15m | 2 x 14.5m | 2 x 15m | 2 x 21m |
| 4 or more | 2 x 13m | 2 x 14.5m | 2 x 15.7m | 2 x 17.2m | 2 x 24m | 2 x 18m | 2 x 17m | 2 x 16m | 2 x 17m | 2 x 23m |